## Cover
Egyptian Maintenance Company
شركة مصر للصيانة
DAILY REPORT
29-08-2019
Project No. : EPROM ( 226 )
| distribution: |  | 1- EPROM Maintenance Manager
2- EPROM Planning Department
supplementary notes:
9
8
7
6
5
4
| 3 | prepared by |  | Planning department
| 2 | reviewed by |  | Site manager
| 1 | approved by |  | Project manager

## Area 02
` |  |  |  |  | Date: | 01-09-2019
Ser | Permit No. | W-O No. | Area | Tag No. | Operator complain | Problem found | Action Taken | Permit Status | Job Status | ND/D/N
1 |  |  | 2B/14 | 14-FISL-150A | Install new | Defective flow switch | new flow switch was installed | Not-Closed | Completed | ND
2 |  |  | 2B/14 | 14-FISL-150B | Install new | Defective flow switch | new flow switch was installed | Not-Closed | Completed | ND
3 |  |  | 2B/14 | 14-FISL-151A | Install new | Defective flow switch | new flow switch was installed | Not-Closed | Completed | ND
|  |  | 2B/14 | 14-FISL-151B | Install new | Defective flow switch | new flow switch was installed | Not-Closed | Completed | ND
4 |  |  | 2B/14 | 14-VSH-004D | PMR | PMR | PMR was carried out | Not-Closed | Completed | N
7 |  |  | 2B/13 | 13-LSLL-069 | Alarm | Defective micro switch | Replace the micro switch with new one the orginal micro switch was hermetically sealed but the new one is not | Not-Closed | Completed | N
2A/05

## Area 04
[5 empty] | Date: | 01-09-2019
S/N | Permit No. | W-O No. | Area | Tag No. | Operator complain | Problem found | Action Taken | Permit Status | Job Status | ND/D/N
1 |  |  | A4/51 | 51-LT-071 | Wrong reading | need calibration | level calibration was done as operator hand dip | Not-closed | completed | ND
2 |  |  | A4/52 | 52-PDIT-011A | PMR | PMR | PMR was done | Not-closed | completed | ND
3 |  |  | A4/52 | 52-PDIT-011B | PMR | PMR | PMR was done | Not-closed | completed | ND
4 |  |  | A4/52 | 52-PDIT-011C | PMR | PMR | PMR was done | Not-closed | completed | ND
5 |  |  | A4/52 | 52-PDIT-011D | PMR | PMR | PMR was done | Not-closed | completed | ND

## Sheet2 (hidden)
Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | Column9 | Column10

## CCTV
Date: 07-08-2019
S/N | Permit No. | W-O No. | Tag No. | Problem Found | Action Taken | Permit Status | Job Status | ND/D/N