## Cover
Egyptian Maintenance Company
شركة مصر للصيانة
DAILY REPORT
29-08-2019
Project No. : EPROM ( 226 )
| distribution: |  | 1- EPROM Maintenance Manager
2- EPROM Planning Department
supplementary notes:
9
8
7
6
5
4
| 3 | prepared by |  | Planning department
| 2 | reviewed by |  | Site manager
| 1 | approved by |  | Project manager

## Area 02
` |  |  |  |  | Date: | 02-09-2019
Ser | Permit No. | W-O No. | Area | Tag No. | Operator complain | Problem found | Action Taken | Permit Status | Job Status | ND/D/N
1 |  |  | 2B/13 | 13-XV-034 | Force | Force | Force the valve to open position then remove force at night. | Not-Closed | Completed | ND
2 |  |  | 2B/13 | 13-XV-038 | Force | Force | Force the valve to open position then remove force at night. | Not-Closed | Completed | ND
3 |  |  | 2B/13 | 13-TE-076 | Install TC | No Problem | Install thermocouple as operation request | Not-Closed | Completed | ND
4 |  |  | 2B/14 | 14-LT-002 | AI | No Problem | Mass balance was carried out | Not-Closed | Completed | ND
5 |  |  | 2B/14 | 14-FT-031 | Probation | No Problem | Mass balance was carried out | Not-Closed | Completed | ND
6 |  |  | 2B/14 | 14-PT-060 | Probation | No Problem | Mass balance was carried out | Not-Closed | Completed | ND
7 |  |  | 2B/14 | 14-TE-039 | Probation | Waiting Scaffolding | Waiting Scaffolding | Not-Closed | In Progress | ND
8 |  |  | 2B/14 | 14-LT-004 | AI | Postponed | Postponed to tommorrow | Not-Closed | In Progress | ND
9 |  |  | 2A/05 | 05-R-01 | ReInstall | No Problem | reinstall hoist accessories then check movement found ok | Not-Closed | Completed | ND
10 |  |  | 2B/07 | 07-LI-225 | Wrong reading | Postponed | waiting the operation to finish filling the tank then recalibrate it | Not-Closed | In Progress | ND
11 |  |  | 2A/05 | 05-XV-019 | Stuck | Defective stem | Check found stuck @ 10% open try to clear stuck by 7 bar but it responds max 25% then at night reforce open and close until fb open signal was found healthy(previously was adjusted at 25% open). Stem rotary guide is found eroded as well as screw guide. | Not-Closed | Completed | D
12 |  |  | 2B/14 | 14-FV-002 | PMR | PMR | Visually check was done | Not-Closed | Completed | N
13 |  |  | 2B/13 | 13-HV-017 | Force | Force | force the valve to close position. | Not-Closed | Completed | N
14 |  |  | 2B/13 | 13-HV-018 | Force | Force | force the valve to close position. | Not-Closed | Completed | N
2A/05

## Area 04
[5 empty] | Date: | 02-09-2019
S/N | Permit No. | W-O No. | Area | Tag No. | Operator complain | Problem found | Action Taken | Permit Status | Job Status | ND/D/N
1 |  |  | A4/51 | 51-MOV-284 | No feedback | No power | Turn on the power, then Check the valve action found ok | Not-closed | completed | ND
2 |  |  | A4/52 | 52-PDIT-021A | PMR | PMR | PMR was done | Not-closed | completed | ND
3 |  |  | A4/52 | 52-PDIT-021B | PMR | PMR | PMR was done | Not-closed | completed | ND
4 |  |  | A4/52 | 52-PDIT-021C | PMR | PMR | PMR was done | Not-closed | completed | ND
5 |  |  | A4/52 | 52-PDIT-021D | PMR | PMR | PMR was done | Not-closed | completed | ND
6 |  |  | A4/51 | 51-LT-002 | PMR | PMR | PMR was done | Not-closed | completed | ND

## Sheet2 (hidden)
Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | Column9 | Column10

## CCTV
Date: 07-08-2019
S/N | Permit No. | W-O No. | Tag No. | Problem Found | Action Taken | Permit Status | Job Status | ND/D/N