## History 02
sn | Tag no | Problem found | complain | Action Taken | status | date
10 | 12-ft-03 | pmr | pmr | pmr was carried | done | 2019-01-01
11 | 05-VSH-112A | PMR | PMR | PMR was carried out | Closed | 06-03-2019
12 | 13-FV-074 | PMR | PMR | PMR was carried out | Closed | 06-03-2019
13 | 14-FV-002 | PMR | PMR | PMR was carried out | Closed | 06-03-2019
14 | 14-VSH-054B | PMR | PMR | PMR was carried out | Closed | 06-03-2019
15 | 02-VSH-002D | Adjust Setpoint | Alarm | Increase setpoint by1/2 turn as requested then function check found ok | Closed | 06-03-2019
16 | 13-FT-058 | Blockage & Condensation | Hunting | Clear blockage from Tx chamber Flushing was done from both sides to clear huge amount of condensation | Closed | 06-03-2019
17 | 15-ME-04C | Defective Teflon ring | No stroke | Stopped, waiting crane | Closed | 06-03-2019
18 | 02-H-01 | Blocked nozzle | Pilot alarm | Clean nozzles and adjust air/fuel ratio | Closed | 06-03-2019
19 | 13-FT-058 | Condensation | Wrong reading | Flushing was done from both sides to clear condensation then check reading found ok | Closed | 06-03-2019
20 | 51-LT-071 | PMR | PMR | PMR WAS DONE | DONE | 06-03-2019
21 | 02-LT-009 | PMR |  | PMR was carried out. Install new cable gland and shroud | Completed | 10-12-2012
22 | 02-LT-010 | PMR |  | PMR was carried out.could not check span as the upper main isolation valve is passing | Completed | 10-12-2012
23 | 02-PT-004 | PMR |  | stopped as the main isolation valve is passing and there is no manifold .ask EPROM shift engineer to transfer the job to static dept. | Stopped | 10-12-2012
24 | 12-FV-050 | PMR |  | PMR was carried out, need shroud . | Completed | 10-12-2012
25 | 02-FT-005A | Check |  | flushing, complet function check was done found ok | Completed | 10-12-2012
26 | 13-LT-031 | wrong reading |  | Replace defective cell then complete calibration was done found ok | COMPLETED | 11-01-2010
27 | 13-LT-032 | Check |  | Function check was done found ok | COMPLETED | 11-01-2010
28 | 13-PT-081 | Check |  | Complete calibration was done | COMPLETED | 11-01-2010
29 | 05-PT-019 | Check |  | Replace the defective manifold and impulse tube then function check was done found ok | COMPLETED | 11-01-2010
30 | 05-PI-243 | Check |  | Stopped as there is no spare parts | waiting spare parts | 11-01-2010
31 | 14-PDT-057 | Wrong reading |  | Clear blockage and complete function check was done found ok | COMPLETED | 11-01-2010
32 | 05-LT-003 | Check |  | Repair the defective connection for communication block card then complete function check was done found ok | COMPLETED | 11-01-2010
33 | 52-PT-22B | Leakage |  | tighten on nuts then function check was done found no leakage | COMPLETED | 11-01-2010
34 | 12-FT-021 | PMR |  | PMR check was carried out | COMPLETED | 11-01-2010
35 | 12-FT-022 | PMR |  | PMR check was carried out | COMPLETED | 11-01-2010
36 | 12-FT-050 | PMR |  | PMR check was carried out | COMPLETED | 11-01-2010
37 | 12-PV-032 | PMR |  | PMR check was carried out | COMPLETED | 11-01-2010
38 | 12-FT-025 | PMR |  | Stopped by STL | STOPPED | 11-01-2010
39 | 12-PV-010 | PMR |  | Stopped by STL | STOPPED | 11-01-2010
40 | 12-PV-025 | PMR |  | Stopped by STL | STOPPED | 11-01-2010
41 | 13-LV-019 | Leakage |  | Tighten on valve packing to stop leakage; Check valve stroke found ok. | Completed | 17-9-2014
42 | 07-PDT-006 | wrong reading |  | Zero and span calibration were done, replace the old manifold by new one with new (1/2 NPT * 12mm) fitting then check reading found ok. | Completed | 17-9-2014
43 | 04-K-02(MP06A) | Check |  | Assist EPROM shift Eng. To check the pump Start/Stop relay. | Completed | 17-9-2014
44 | 04-K-02A | Survey |  | Survey was done for tag no. found the following: missing:TE-653A,C&TE-115A,B.C&TE-30A,B,C&TSH-614B,650E&LSL-603A,B&TE-114B,28B. Clean:XYV-623,627,622,625,626,620,628 & PSL-632,634,645 & PSLL-635,633,631 & TE-28A,113,655,626,635,652E,F,G,H,A,B,C,D &TE-650F,E,D,B,C. Replace: TSH-614A,653B & PSL-630 & PSLL-616,615. Modify: TSH-614C,B & 652L,J,I,K. | Completed | 17-9-2014
45 | 51-LIT-071 | PMR |  | PMR was carried out. | Completed | 17-9-2014
46 | 13-FT-091 | Wrong reading |  | Reset, Zero / Span calibration were done, Remove the defective display, flush from manifold was done then check reading found ok. | Not closed | 20-04-2016
47 | 07-PT-021 | Wrong reading |  | Zero / Span calibration were done several times till the transmitter accept then check reading found ok. Note: install new U-bolt for the mounting bracket and needs 2 cover o-rings. It is recommended to replace the transmitter and its mounting bracket by new ones, replace the whole impulse tube with its 2 fittings (1/2" NPT * 12mm Tube) | Not closed | 20-04-2016
48 | 13-TE-065,066 | Wrong reading |  | Check elements and loop were done found ok. Swap the elements found the reading as before. Note: there is a problem in TE-066 thermowell and needs to be checked ,waiting S/D. | Not closed | 20-04-2016
49 | 13-XV-030 | Stuck |  | Clear valve stuck by force open /close ,check regulator found continuously vent, increase the regulator o/p then check valve open / close found ok, and replace the air regulator with an old one then check valve stroke found ok | Not closed | 20-04-2016
50 | 15-LT-004 | Install new HF module |  | dismantle the Tx and Install a new HF module, Factory calibration as done at EMC w/s, install again and custom mapping were done then check reading found ok. | Not closed | 20-04-2016
51 | 13-XV-029 | Stuck |  | check found the valve is stuck at open, dismantle the actuator and check found it ok, check the valve body found it moving hardly, needs to be dismantled to carry out maintenance but operation department refused so its waiting for shutdown. | Not closed | 20-04-2016
52 | 07-FT-019 | Wrong reading |  | Zero check, Span calibration, flush tube were done then check reading found ok. | Not closed | 20-04-2016
53 | 13-PT-054 | Blockage |  | Reset power and clear blockage were done then check reading found ok. | Not closed | 20-04-2016
54 | 13-FT-091 | Wrong reading |  | Replace the electronic Module with an old one then check reading found ok. | Not closed | 20-04-2016
55 | 51-FT-030 | Wrong reading |  | dismantle the turbine and clean it with steam, jhkgg vddfveaverg egg sefgs f s f df vsf vgrbb g rdg d g dfgbdgfb bdfbdf gbdb f d b, bsfgbsg. Bfbfbfgbdf sfbdgb .h nd gdgnd . Df gd bdf bg dn hthnfhndghnnf ng nn nfg fn . | Not closed | 20-04-2016